## Investment Priorities
| Town | The proposed ECM description | Annual energy savings, kWh | Annual energy Consumption of Water Utility, kWh | Savings in %, as compared to total consumption | Capital investment cost, MDL | Simple payback period, years | Urgency of Investment for the town | Incremental Grant Investment, MDL | Incremental Grant Investment, USD | 11.91 | USD/MDL
BASIC PACKAGE | Balti | Optimization of existing water supply scheme from Soroca-Balti reservoirs | 3700000 | 10044651 | 36.84% | 0 | 0 | 1 | 0 | 0
| Causeni | Replacement of submersible pump in the well no. 2 | 127458 | 679229 | 18.77% | 198660 | 0.9 | 2 | 198660 | 16680.1008
| Floresti | Replacement of submersible pump in the wells nos. 5,7,10,12 | 212145 | 1242453 | 17.07% | 707190 | 1.9 | 1 | 905850 | 76057.9345
| Balti | Optimization of pumping scheme Decebal – Upper reservoirs - Baza | 1113600 | 10044651 | 11.09% | 916575 | 0.5 | 2 | 1822425 | 153016.3728
| Orhei | Modifications of Jeloboc Water Main and PS6 | 182795 | 1900344 | 9.619% | 2234720 | 6.8 | 2 | 4057145 | 340650.2939
| Cahul | Hydraulic optimization of PS 3: - Spirin pumping zone - city pumping zone | 186821 | 1958300 | 9.54% | 1027125 | 3.0544 | 1 | 5084270 | 426890.848
| Causeni | Water supply distribution network optimization | 63080 | 679229 | 9.287% | 1540000 | 13.6 | 1 | 6624270 | 556193.9547
| Causeni | Replacement of submersible pump in the well no. 1 | 40909 | 679229 | 6.023% | 145860 | 2 | 3 | 6770130 | 568440.806
| Floresti | Replacement of pumps at PS 2 | 56093 | 1242453 | 4.515% | 816585 | 8.1 | 3 | 7586715 | 637003.7783
| Ungheni | Modification of pumping at PS 1 | 78752.4 | 1820853 | 4.325% | 443850 | 3.1 | 1 | 8030565 | 674270.7809
| Orhei | Implementation of SCADA system | 80173 | 1900344 | 4.219% | 1881600 | 2.9 | 1 | 9912165 | 832255.6675
| Floresti | Replacement of pump at PS 3 | 48253 | 1242453 | 3.884% | 421575 | 4.9 | 2 | 10333740 | 867652.3929
| Balti | Cogeneration plant for electrical and heat power production | 337869.4444 | 10044651 | 3.364% | 1922702 | 3.2 | 3 | 12256442 | 1029088.3291
| Floresti | Sewage pump for SPS Main | 41186 | 1242453 | 3.315% | 509850 | 6.9 | 5 | 12766292 | 1071896.8934
| Floresti | Replacement of damaged disk aerators at WWTP | 27000 | 1242453 | 2.173% | 320000 | 6.6 | 4 | 13086292 | 1098765.0714
ADDITIONAL SMALL INVESTMENTS | Cahul | Installation of new pump at PS 5 | 29591 | 1958300 | 1.511% | 31020 | 0.6 | 2 | 13117312 | 1101369.6054
| Causeni | Transformer replacement at WWTP | 9000 | 679229 | 1.325% | 54000 | 3.3 | 5 | 13171312 | 1105903.6104
| Balti | Replacement of pump at BPS Iorga 6 | 26200 | 10044651 | 0.2608% | 61050 | 1.3 | 6 | 13232362 | 1111029.555
| Causeni | Replacement of pump at D. Cantemir BPS | 1478 | 679229 | 0.2176% | 7000 | 2.6 | 4 | 13239362 | 1111617.2964
| Ungheni | Replacement of pumps at BPS Nationala 43 | 5299.8 | 1820853 | 0.2911% | 61050 | 6.4 | 3 | 13300412 | 1116743.241
| Balti | Replacement of active sludge recirculation pump | 210000 | 10044651 | 2.091% | 1010000 | 2.7 | 4 | 14310412 | 1201545.9278
| Floresti | Speed control for air blower at WWTP and - Installation of sludge pumps in secondary clarifiers | 25200 | 1242453 | 2.028% | 340000 | 7.4956 | 7 | 14650412 | 1230093.3669
| Balti | Speed control for air blower at WWTP | 184000 | 10044651 | 1.832% | 380000 | 1.1 | 5 | 15030412 | 1261999.3283
| Cahul | Hydro-turbine at WWTP | 32850 | 1958300 | 1.677% | 567600 | 9.6 | 4 | 15598012 | 1309656.759
| Ungheni | Replacement of pumps at BPS Cristiuc 11 | 22863.6 | 1820853 | 1.256% | 201300 | 4.9 | 2 | 15799312 | 1326558.5223
| Cahul | Installation of new sludge pump at WWTP | 19710 | 1958300 | 1.006% | 218625 | 6.2 | 3 | 16017937 | 1344914.9454
| Orhei | Replacement of pumping stations external lighting lamps | 18923 | 1900344 | 0.9958% | 122000 | 3.6 | 3 | 16139937 | 1355158.4383
| Floresti | Sewage pump for SPS 1 | 10877 | 1242453 | 0.8754% | 193875 | 9.9 | 6 | 16333812 | 1371436.7758
| Ungheni | Replacement of pumps at BPS Nationala 33a | 1708.2 | 1820853 | 0.09381% | 61050 | 19.9 | 4 | 16394862 | 1376562.7204
1 USD = 11.91 MDL
Note on C7: User: Two investments merged
Note on D14: User: Equivalent in kWh